Form FCS1

Fume Cupboard selection assessment

| This form is intended to document the risk assessment process that must take place in order to determine the specification of new fume cupboards. It also ensures that the brief provided to manufacturers is clearly presented and that the user’s requirements are detailed. As fume cupboards are responsible for a significant amount of energy consumption, this process is now also in place to ensure that all new fume cupboards installed at Imperial College are specified so as to be as energy efficient as possible. This assessment must be approved by the relevant Departmental, Campus or Faculty Safety Officer/Manager, the Chief Fire Officer and the Safety Department including when a cupboard is to be used for radiation work, by the Safety Department Radiation Protection Team. Once completed and reviewed this form must be submitted to the relevant Project Manager or User co-ordinator. |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Name of person in control of the work carried out in this fume cupboard |  |  |  |  |  |  |  |  |  |  |  |
| Name: |  |  |  |  |  | Section/Institute/Dept/: |  |  |  |  |  |
| Location of cupboard |  |  |  |  |  |  |  |  |  |  |  |
| Room: |  |  |  |  |  | Building: |  |  |  |  |  |
| Campus: |  |  |  |  |  | Fume cupboard reference: |  |  |  |  |  |
| Work to be conducted within the fume cupboard |  |  |  |  |  |  |  |  |  |  |  |
| What will the fume cupboard mainly be used for? |  |  |  | *Open processes |  |  |  |  |  | **Enclosed processes |  |
| * Open processes - predominantly open apparatus, deliberate evaporations (particularly those involved with heating) etc. ** Enclosed processes - predominantly routine transfers and enclosed apparatus / equipment etc. |  |  |  |  |  |  |  |  |  |  |  |
| What hazardous substances will be used? |  |  |  |  |  |  |  |  |  |  |  |
| Flammables: | Example of most hazardous: |  |  |  |  |  |  |  | Max quantity: |  |  |
| Highly reactive substances: | Example of most hazardous: |  |  |  |  |  |  |  | Max quantity : |  |  |
| Corrosives: | Example of most hazardous: |  |  |  |  |  |  |  | Max quantity : |  |  |
| Radioisotopes: | Example of most hazardous: |  |  |  |  |  |  |  | Max quantity : |  |  |
| Pyrophorics: | Example of most hazardous: |  |  |  |  |  |  |  | Max quantity : |  |  |
| Explosives: | Example of most hazardous: |  |  |  |  |  |  |  | Max quantity : |  |  |
| Carbon nanomaterials: | Example of most hazardous: |  |  |  |  |  |  |  | Max quantity : |  |  |
| Toxics: | Example of most hazardous: |  |  |  |  |  |  |  | Max quantity : |  |  |
| Do the processes to be undertaken have any of the following properties? Distillation Naked flames High heat production Can be perturbed by fume cupboard airflows Cable or pipework connections to outside of the cupboard Fans or external moving parts Large items of equipment? Very dusty processes System(s) under pressure If any of the above properties do apply to your process, provide details: |  |  |  |  |  |  |  |  |  |  |  |
| Fume cupboard features (answer all questions and select all those applicable) |  |  |  |  |  |  |  |  |  |  |  |
| Size (width in mm): |  | Ducted or recirculating |  |  |  |  |  | Walk-in or conventional |  |  |  |
| Sink: |  |  | If required, specify size (mm) and any special features: |  |  |  |  |  |  |  |  |
| Water: |  |  | If required, specify type and any special features: |  |  |  |  |  |  |  |  |
| Power: |  |  | If required, specify type and any special features: |  |  |  |  |  |  |  |  |
| Other services: |  |  | If required, specify type and any special features: |  |  |  |  |  |  |  |  |
| Scaffolding : |  |  | If required, specify size (mm) and any special features: |  |  |  |  |  |  |  |  |
| Ventilated solvent storage: |  |  | Approximate quantity of flammable liquid to be held in the laboratory: |  |  |  |  |  |  |  |  |
|  |  |  | BS476 cabinet: Minimum standard |  |  |  | BS14470 Pt.1 cabinet: Higher standard |  |  |  | Size: |
|  |  |  | Other chemicals requiring ventilated storage? |  |  |  |  |  |  |  |  |
| HEPA filter required: |  |  | If required, state reason: |  |  |  |  |  |  |  |  |
| Other filter required: |  |  | If required, state reason: |  |  |  |  |  |  |  |  |
| Worktop material: |  |  | Material required: |  |  |  |  |  |  |  |  |
| All other interior wall/ceiling material: |  |  | Material required: |  |  |  |  |  |  |  |  |
| Lead lining: |  |  | If required, detail where required and thickness: |  |  |  |  |  |  |  |  |
| Reinforced structure: |  |  | If required, state reason: |  |  |  |  |  |  |  |  |
| Seamless interior with rounded corners: |  |  | If required, state reason: |  |  |  |  |  |  |  |  |
| Dedicated duct runs required: |  |  | If NOT required, state what these can be shared with: |  |  |  |  |  |  |  |  |
| Drain material specification: |  |  | If particular required, provide details: |  |  |  |  |  |  |  |  |
| Dedicated drainage straight to stack: |  |  | If required, state reason: |  |  |  |  |  |  |  |  |
| Drain catchpot or trap: |  |  | If not required or with any special features, please detail these: |  |  |  |  |  |  |  |  |
| Fire suppression systems: |  |  | Fire suppression systems should be installed for all new fume cupboards where a fire risk may exist. If fire suppression systems are not required then explain why: If a fire suppression system is required, are any of the following extinguishing agents incompatible with the materials that may be used within the cupboard? Inerting gases Chemical gases dry chemical powders foam |  |  |  |  |  |  |  |  |
| Other features required: |  |  |  |  |  |  |  |  |  |  |  |
| Extract ductwork ( n/a if recirculating cupboard is required) |  |  |  |  |  |  |  |  |  |  |  |
| Are any of the following ductwork materials incompatible with the processes or substances to be used in the fume cupboard? PVC Polypropylene GRP clad polypropylene Stainless steel Galv steel |  |  |  |  |  |  |  |  |  |  |  |
| Energy saving features |  |  |  |  |  |  |  |  |  |  |  |
| In-flow velocity: The default is 0.35m/sec. If higher is required specify the velocity and explain why required: |  |  |  |  |  |  |  |  |  |  |  |
| Confirm the nature of the HVAC air supply system: Mechanically ventilated Naturally or passively ventilated |  |  |  |  |  |  |  |  |  |  |  |
| Will the fume cupboard need to be run overnight or for long periods of time during the day without a worker at the cupboard? Yes No |  |  |  |  |  |  |  |  |  |  |  |
| Can the fume cupboard be switched off when not in direct use? Yes No |  |  |  |  |  |  |  |  |  |  |  |
| Is this HVAC system being refurbished or replaced as part of this fume cupboard installation? Yes No If yes, provide name of the Project Manager: |  |  |  |  |  |  |  |  |  |  |  |
| Can any of the following energy saving measures NOT be considered? |  |  |  |  |  |  |  |  |  |  |  |
| Auto-sash closers with Variable Air Volume controls Variable Air Volume controls with manual sash |  |  |  |  | Auto-sash closers with fan-speed controller Fan-speed controller with manual sash |  |  |  |  |  |  |
| If any of the above cannot be installed please provide an explanation: |  |  |  |  |  |  |  |  |  |  |  |

| Approvals Note that whilst signatures are not required on this form it remains the responsibility of the person completing this to ensure that those persons named below have reviewed this assessment |  |  |
| --- | --- | --- |
| Person completing this form |  |  |
| Name: | Section/Institute/Dept/: | Date: |
| Safety Officer (DSO/FSM/CSM) |  |  |
| Name: | Dept/Faculty/Campus: | Date: |
| Chief Fire Officer |  |  |
| Name: |  | Date: |
| Safety Department |  |  |
| Name: | Position: | Date: |
| Radiation Protection Team (for cupboards in Controlled Areas) |  |  |
| Name: | Position: | Date: |